Water–Vapor treatment of Shower Systems in healthcare facilities: An effective protocol to contain the risk of exposure to Legionella of at-risk patients

Tian You1†, Pryanka Parmar1†, Guillaume Decke2, Kyle Baikie1, Lilian Ryckewaert1,2, Alexis Marette2, Hélène Niculita-Hirzel1*

Material and Methods

Experimental design

Shower systems were installed in replicate across 5 different settings. In the healthcare facility in Lausanne (University hospital of Lausanne, Switzerland) and in the nursing home in St-Etienne (France) shower units were installed in triplicate for each treatment condition (no treatment, water-vapor treatment, or conventional thermal disinfection) and for each biofilm age targeted for sampling. In the domestic settings, three residential setting located in Nods, Nidau and Prêles (Switzerland) were selected based on the presence of at least two independent shower cabins per building, allowing for paired comparisons between treated and untreated conditions.

At 5 weeks, 32 weeks, 52 weeks and 104 weeks, shower systems were collected. In locations other than Lausanne, volunteers were instructed to detach the shower hoses from all fittings. After removal, the hoses were filled with tap water to preserve moisture on the internal surfaces, sealed with screw caps, and transported to the laboratory within 24 h. Once in the laboratory, paired biofilms were either directly extracted or subjected to a single water-vapor treatment. In the experimental shower of Unisanté’s laboratory, paired biofilms were either directly extracted or subjected to a single treatment either water-vapor treatment or thermal disinfection prior to extraction. To assess the effects of repeated weakly water-vapor treatments, biofilms aged 32 weeks were treated once per week for four consecutive weeks, one sample was extracted after each treatment.

The efficacy of the treatment in removing biofilm from hoses was visualized by scanning electron microscopy on 1x1 cm2 sections cut from both extremities and the center of each hose. Biofilms from the remaining hose sections were extracted. Total cell counts were determined by flow cytometry using SYBR green and PicoGreen-stained aliquots, and metal concentration by inductively coupled plasma mass spectrometry (ICP-MS) following previously published protocols. Microbiome community composition was assessed by 16S rRNA gene amplicon sequencing targeting the V3-V4 regions, using the Illumina MiSeq plateform, when sufficient DNA was available. ICP-MS analysis was performed by the Forensic Toxicology and Chemistry Unit (UTCF) at CHUV, and sequencing by Microsynth (Switzerland).

Shower system characteristics and treatment conditions

Each shower system was composed of a Polyvinyl Chloride (PVC) flexible shower hose (180 cm long and of a diameter of 9 mm), and a low water and energy consumption showerhead with six 1.1 mm nozzles based on water-atomizing technology. The water flow is 5.2 L/min.

The protocol of water-vapor treatment consisted in an automated sequence alternating between flash of tap water and 120℃ high-pressure vapor injection through the shower hose initiated at the water inlet connection point. The vapor was generated with a Swiss commercial steam machine (Power (W) 2200, water-heating time=3 min, volume=1 L). The sequence consisted in, first, a flush of water at 37℃ for 10 seconds, then an injection of high pressure vapor for 30 seconds. The water-vapor cycle is repeated 4 times. After the 4th cycle, water flash into the hose for 10 seconds followed by 1 minutes of high pressure vapor at 120℃.

The protocol of hot water disinfection consisted in running hot water at 65°C for 10 min.

Conditions of Biofilm growth

The shower systems were vertically hung. A shower event was run for three minutes during working days (five days a week) with a water temperature of 37 °C ± 2 °C to allow biofilm growth in shower systems. The system does not allow for the draining of water in the shower system.

Biofilm Visualization with Scanning Electron Microscopy

1x1 cm2 sections cut from both extremities and the center of each hose were prepared for scanning electron microscopy (SEM). Samples were fixed in 2.5% Glutaraldehyde / Cacodylate buffer (0.1 M, pH 7.2) and stored at 4°C. Prior to imaging, the fixed samples were washed three times for 3 minutes with 1 mL of 0.05 mM sodium cacodylate buffer, dehydrated through serial concentration of ethanol 25%, 50%, 75%, followed by two washes in 100% ethanol for 5 min each. Dehydrated samples were air-dried overnight at room temperature. The following day, the samples were mounted on 25 mm double sided adhesive conductive carbon discs and carbon-coated in a Leica EM CED 030. Additional conductivity was ensured by applying silver conductive glue to the edges of the samples. SEM imaging was performed using a Phenom XL scanning electron microscope operated at an acceleration voltage of 5 kV. For each sample, one image was captured at 1000× magnification to define the general area of interest. Within this area, five additional images were acquired at 4000× magnification from randomly selected locations.

Biofilm extraction from hoses

The overall length of hoses of 180 cm long and of a diameter of 9 mm was used for biofilm removal via repeated sonication as previously described (Parmar et al., 2023). Briefly, the method consisted in plug an adapted stopper at one end of each hose section, fill the hose section with sterile glass beads (3 mm diameter) and 0.2 μm filtered mineral water (Evian, France), seal the other extremity of the hose section with a sterile stopper, and invert ten times. Then, to detach the biofilm, the hose sections were sonicated by submersion in a sonication bath (Branson 5210, Branson, USA) for 5 min. The biofilm suspension was collected in 50 mL tubes (VWR International, USA) by removing the stopper from one end gently inverting the hose section, taking care not to lose glass beads during the process. and the hose sections refilled with freshly filtered mineral water. Subsequently, the hose sections were refilled with freshly filtered mineral water to repeat the steps of sonication. The sonication and collection steps were performed a total of five times. Finally, the total biofilm suspension (overall volume ranging between 80 and 100 mL) was sonicated for 1 minute before further analyses.

Flow cytometry assay

The flow cytometry assay (FCA) profiles of the samples were obtained by using a combination of SYBR fluorescence for all cells (with damaged and non-damaged membranes) and PI red fluorescence for cells with damaged membranes using a CYTOFLEX S2 (Beckman Coulter, US). Two hundred microliters of biofilm were labeled with 1 l of propidium iodide (PI) at 1 mg·mL-1 (Invitrogen P3566, Life Technologies Europe BV, Zug, Switzerland) and with 2 μl of SYBRTM Green I nucleic acid gel stain (SYBR) diluted 100x (Invitrogen S7563, Life Technologies Europe BV, Zug, Switzerland A volume of 40 µl was measure at a medium sheath flow velocity of 30 µL·min-1. When needed, biofilms suspensions were diluted with filtered PBS (VWR Chemicals, USA) to do not exceed 105 cells·ml-1). The SYBR signal was detected in the FITC-H channel (488 nm excitation and 525 nm acquisition), and the PI signal was detected in the APC channel (640 nm excitation and 660 nm acquisition). Data analysis was performed using the FlowJoTM software (version 10.9.0, Ashland, USA). Manually set gates for intact and damaged cells were applied for each sample based on SYBR and PI fluorescence alone, as well as on the intrinsic fluorescence of unstained sampled. Intact cells were considered viable, and damaged cells were considered dead.

Elementary Analysis of Biofilms Suspensions

The samples were screened for the presence of metals, and those with significant concentration (44Ca, 107Ag, 57Fe, 63Cu, 66Zn, and 208Pb) were quantified using ICP-MS as previously described. Briefly, 2.5 mL aliquots of each sample were subjected to acid digestion in 65% HNO3 at a temperature of 95 °C for 25 min. After the digestion process, 25 mL of high-purity water MilliQ was added to each sample. The elemental concentrations were quantified using an ICP-MS Thermo iCAP TQ. Standards were provided by SCP Science (Courtaboeuf, France) and Fluka (Merck KGaA, Darmstadt, Germany). The limits of detection and limits of quantification are indicated in Table 1. The ICP-MS analysis was conducted by the Forensic Toxicology and Chemistry Unit at Vaud University Hospital (CHUV).

Table 1. Limit of detection (LOD) and limit of quantification (LOQ) of metals detected in samples.

|  | 44Ca 1 | 57Fe 1 | 63Cu 1 | 66Zn 1 | 107Ag 1 | 208Pb 1 |
| --- | --- | --- | --- | --- | --- | --- |
| LOD | 33.3 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 |
| LOQ | 100.0 | 20.0 | 20.0 | 20.0 | 20.0 | 20.0 |

1 Expressed in μg·L−1.

DNA extraction

Genomic DNA was extracted from 500 µL of biofilm using the FastDNA SPIN kit (MP Biomedicals), following the manufacturer's protocol with slight modifications Specifically, mechanical lysis was performed using a TissueLyser II (Qiagen, Germany) to improve cell disruption efficiency.  DNA concentration was quantified using the Quant-iT™ PicoGreen™ dsDNA Assay Kit (Thermo Fisher Scientific) , and fluorescence measurements were carried out on a Tecan Infinite® 200 PRO microplate reader (Tecan Group Ltd.).

Library preparation and sequencing:

Amplicon libraries targeting the V3–V4 region of the 16S rRNA gene were prepared using a two-step PCR protocol (1st Step PCR of 20 cycles and 2nd Step PCR of 10 or 12 cycles) with Illumina Nextera barcoded primers. Following amplification, libraries were purified, quantified, and pooled in equimolar concentrations. Sequencing was performed on an Illumina MiSeq platform using the v2 chemistry (2 × 250 bp paired-end reads). Raw reads were subsequently demultiplexed and trimmed to remove any remaining Illumina adaptor sequences using standard bioinformatics pipelines.

Bioinformatics Analysis of 16S rRNA Gene Amplicon Sequencing Data

Six samples collected after treatment were excluded from 16S rRNA gene amplicon sequencing due to insufficient cell counts, which resulted in insufficient genomic DNA for sequencing. Sequencing generated paired-end FASTQ files, which were processed using a standardized bioinformatics pipeline implemented in the dada2 package in R (Callahan et al., 2016).

First, we checked the quality of raw sequencing reads using the plotQualityProfile. The forward and reverse reads were then filtered and trimmed using filterAndTrim. Amplicon Sequence Variants (ASVs) were inferred as follows: error rates were learned from the filtered reads using learnErrors, and sequence denoising was performed on both forward and reverse reads. Paired-end reads were merged using mergePairs, and a sequence table was generated using makeSequenceTable. Finally, chimeric sequences were identified and removed usinf removeBimeraDenovo with the consensus method. Out of 11,385 input sequences, 9,931 chimeras were detected and removed. ASVs were taxonomically assigned using the SILVA ribosomal RNA gene database (v138.1) (McLaren and Callahan, 2021; Quast et al., 2013). The assignTaxomy function was used to assign genera, and addSpecies was used to assign species using the SILVA species database. The resulting ASV table, taxonomy table and metadata were exported as CSV file for downstream analyses. An additional six post-treatment samples were excluded from further analysis due to insufficient ASV counts. A total of 15 ASVs were assigned to the Legionella genus (ASV281, ASV353, ASV737 belong to L. anisa, ASV346 belong to L. worsleiensis, ASV389, ASV572, ASV587, ASV1223 belong to L. pneumophila, ASV647 belong to L. rowbothamii, ASV1069, ASV1344 belong to L. qingyii, ASV1239 belong to L. norrlandica, ASV580, ASV1122, ASV1227 are uncultured L. spp.).

Microbial community analysis was performed using the R package phyloseq (Callahan et al., 2016). Metadata, ASV taxonomy and ASV abundance tables were imported. Two Phyloseq objects were created by combining the processed ASV abundance table (relative abundance and absolute abundance), taxonomy table, and metadata.

Alpha diversity (Observed, Shannon, Simpson) was calculated from the raw ASV data (relative abundance table). Diversity metrics were examined across Treatment, Biofilm age, Location, and presence or absence of L. pneumophila. Alpha diversities including observed ASVs, Shannon index, and Simpson index were plotted. Statistical significance was assessed using the Kruskal-Wallis test followed by Dunn’s post hoc test (Avalos-Fernandez et al., 2022; Cassol et al., 2025; Kers and Saccenti, 2022). The top 30 genera were identified and visualized using stacked bar plots and heatmaps, including log-transformed data. Faceted plots were generated to allow metadata-driven comparisons (Gloor et al., 2017; Tkacz et al., 2018).

β-Diversity was evaluated using with Jaccard distances, Bray-Curtis distances, Unweighted Unifac distances and Weighted Unifac distances. Ordination plots were generated to compare microbial communities based on Treatment, Location, Biofilm age and the presence or absence of L. pneumophila. PERMANOVA was used to assess significant group differences, supported by relative abundance and variance-stabilized data. Genus richness was also analyzed by filtering, counting, and visualizing unique genera per sample.

The analysis of metal ions such as calcium (Ca), copper (Cu), and iron (Fe) followed a three-step process. First, metal concentrations were log-transformed, missing values were removed, and categorical metadata variables were converted into factors. Second, alpha diversity metrics (Observed ASVs, Shannon index, Simpson index) were computing using the phyloseq package, merged with the metal ion dataset, and visualized via scatter plots with Pearson correlation coefficients to assess relationships. Third, beta diversity was analyzed by computing Bray-Curtis dissimilarities, followed by PERMANOVA to test for effects of metal ions and sample groupings (e.g., Treatment, Location). Ordination plots (PCoA, NMDS) with environmental vector fitting were used to visualize associations between microbial community structure and metal ion concentrations.

Functional profiles of microbial communities were inferred from the 16S rRNA gene data using PICRUSt2 pipeline (v2.6.2)18. To do so, the ASV abundance table and representative sequences were used as input. ASVs were placed into a reference phylogeny, followed by hidden-state prediction of gene families. The predicted metagenome was stratified to obtain KEGG Orthology (KO) abundances, and pathway-level abundances were subsequently inferred. The accuracy of the predictions for each sample was assessed using the weighted Nearest Sequenced Taxon Index (NSTI). To determine the impact of different interventions on the functional potential of the biofilm community, we performed a differential abundance analysis on the KEGG Orthology (KO), Enzyme Commission number (EC) and Pathway abundance table generated by PICRUSt2. The analysis was conducted using the ANCOMBC R package, implementing the ANCOM-BC2 algorithm20. KOs, ECs and pathways with a Benjamini-Hochberg adjusted p-value of < 0.05 were considered significantly differentially abundant.

The influence of metal ions (including Ca, Cu, Fe, Zn, Ag, and Pb) on microbial diversity was investigated. Metal concentrations underwent log transformation. The link between alpha diversity indices (such as Observed ASVs, Shannon index, and Simpson index) and the log - transformed metal data was examined. This was done using Pearson correlation analysis and scatter plots. To assess beta diversity, Bray - Curtis distances were calculated. PERMANOVA was used to examine how metals and factors like treatment and sampling location affected the microbial community. Ordination plots, specifically PCoA and NMDS, along with envfit analysis, were used to emphasize the impact of metals on the microbial community structure. All these statistical and visualization analyses were carried out in the R environment with the help of packages such as phyloseq, vegan, and ggplot2.

Spearman correlations were calculated between the summed abundance of L. pneumophila and L. anisa and the top 30 other genera, across all samples and untreated samples separately. Genera showing significant correlations with L. pneumophila and L. anisa were further analyzed. Changes in their log-transformed abundance across treatment groups were tested using Kruskal-Wallis and pairwise Wilcoxon tests.